DOCUMENTATION OF LIQUINET PROGRAM

Basic Concepts

The Program is based on paper “Application of Finite Element computer Program to Water Distribution System Analysis” by Anthony G. Collins. In this program, we have used Darcy Weisbach Equation. Attempts have been made to take into account the effects of Partial closure of Valves and effects of Booster/Pumps on a Pipe Network.

Formulae Used:

For Pipe Segments

h={fLq sup{2}} over {2gdA sup{2}}+{kq sup{2}} over {2gA sup{2}}

 Here, h=Head Loss,
f=friction factor,
L=Length,
q=Flow Rate,
g=Gravitational Acceleration,
d=Diameter,
A=Area of Pipe calculated by %PI {d^2} over {4} ,
k=Total k factor of Pipe taking into account bend, reducers, valves, etc.

For Boosters

 h={q sup{2}} over {2gA sup{2}}-H_d

Here, h=Static Head Difference,
Hd=Total Head created by the Booster,
q=Flow Rate,
g=Gravitational Acceleration,
A=Area of Pipe calculated by %PI {d^2} over {4} ,

For Flow Control Valves

h={kq sup{2}} over {2gA sup{2}} times {left( 100 over o right )} sup {2n}

Here, h=Head Loss,
k=Total k factor of Pipe taking into account bend, reducers, etc.,
g=Gravitational Acceleration,
d=Diameter,
A=Area of Pipe calculated by %PI {d^2} over {4} ,
o=opening percentage,
n=non-linearity factor.

Background of using Flow Control Valve Formula

For Valves, it is not necessary that flow within the valve be directly proportional to the opening percentage. It may be linear or non-linear (including quick opening and equal percentage).
Solving for q in the formula provided for flow control valve we have,

q={A(o/100)^n} times {(2hg over k)}^{1/2}

Using the above formula, by initializing ‘n’ as .5, 1, 2 each time, we plot a graph to find the following characteristics for different opening percentages.
Here, the blue line represents n=.5, green line represents n=1, and red line represents n=2.

An Octave/Matlab program “valve_characteristic.m” used to plot this has been provided in the source files, in the Documentation folder. In the program Diameter, Head Loss, k-factor and gravitational acceleration has been considered as 1 meter, 10 meters, 10 and 9.81 m2/s respectively. Hence, a reasonable approximation of flow characteristics of the valve may be represented if adequate data is available.
Working Principle

The program tries to approximate the solution by linearising the equation similar to the Matrix form left [ F right ]=left [ K right ] left [ x right ] as left [ Q right ]= left[ C right ]left[ H right ]. Here Q is the amount of flow in or out of a particular node. H is the head at a certain node.

Method of Calculation for Each Element

In local form, similar to the form f=kx, q=ch has been considered where q is the flow through the particular element and h is the head loss.
We know from Darcy Weisbach equation that h={flq^2} over { 2gdA^2 }. For sake of better understanding, lets consider the previous equation as h={q^2} over { k }.
Now consider that h is known and q is to be found by using q=ch.

Refer to the graph above. We start of with an approximated value of q1 In the program, this accomplished by asking the user for an approximate value of Reynold’s number from where q1 is calculated.
- Step 1.
  - h1 Is calculated by h1={q1^2} over { k } and slope c1={h1} over { q1 }.
- Step 2
  - Using the slope of c1 we calculate qc as qc=c1 times h.
- Step 3
  - hc={qc^2} over k And slope cc=hc over qc
- Step 4
  - If hc is within approximation range, we stop calculating. Else, we find new slope c2={c1+cc} over 2 and continue to Step 5.
- Step 5
  - q2=c2 times h. We go back to Step 1 and continue the later Steps. h2 Is calculated by replacing h1. q1 Is replaced by q2, and c1 is replaced by c2.

These steps are repeated for every element in each iteration. The instance of the iteration runs till h_1, h_2 " and " h_3 for all elements are within the allowed approximation range.

Formation of Global Matrix

To demonstrate how the global matrix is formed we consider a simple problem given below.

Circles with numbers indicate nodes. Flows {Q_1}, { Q_2 }" and "{ Q_3 } are going into the nodes 1, 2, and 3. If the flow is going into the node (is going into to the pipe network), the value of {Q_1}, { Q_2 } "or " { Q_3 } shall be positive. If the flow is coming out of the node (is coming out of the pipe network), the value of {Q_1}, { Q_2 } "or " { Q_3 } shall be negative.
Flows within the pipe are represented by { q_1 }, { q_2 }" and "{ q_3 }. Flow towards a particular node is taken as positive. Flow away from a node is negative.
It is to be noted that head loss within an element or static head difference across any element(as in case of Boosters) is the difference of the Heads of the two nodes at the end of the particular element. Hence, we may write the following as per the flow direction of the liquid.

h_1 =H_1 - H_2	…..(a)

h_2 =H_2 - H_3	…..(b)

h_3 =H_3 - H_1	…..(c)

Where H_1, H_2 " and " H_3 are the Heads at nodes 1, 2, 3 respectively. Hence, we may form the following equations for each element.

q_1 = c_1( H_1 - H_2) + c_1 H_d1	…..(1)

q_2=c_2( H_2-H_3 ) + c_2 H_d2	…..(2)

q_3=c_3( H_3 - H_1 ) + c_3 H_d3	…..(3)

Above, H_d2 " and " H_d3 are equal to zero(0).
We have the following equations at each node. Q_1, Q_2 " and " Q_3 Are considered positive below, for the sake of explanation.

Q_1 -q_1+q_3 = 0 newline rightarrow Q_1 = q_1 - q_3	…..(4)

Q_2 - q_2 + q_1=0 newline rightarrow Q_2 = q_2-q_1	…..(5)

Q_3 + q_2 - q_3 =0 newline rightarrow Q_3 = q_3 - q_2	…..(6)

Substituting Equations (1), (2) & (3) in (4), (5) & (6) as appropriate, we have the following.

Q_1 =(c_1+c_3) H_1 -c_1 H_2 - c_3 H_3 + c_1 H_d1 - c_3 H_d3	…..(7)

Q_2 = -c_1 H_1 + ( c_1 + c_2 ) H_2 -c_2 H_3 -c_1 H_d1 +c_2 H_d2	…..(8)

Q_3 = -c_3 H_1 - c_2 H_2 + ( c_3 + c_2 )H_3 + c_3 H_d3 - c_2 H_d2	…..(9)

From equations (7), (8) & (9) we can form the following matrix.

left [ matrix{Q_1 ##Q_2 ##Q_3 } right ] = left[ matrix{c_1+c_3 #-c_1#-c_3##-c_1# c_1+c2 #-c2## -c_3# -c_2 # c_3+c_2} right ] left[matrix{H_1##H_2##H_3} right]+ left [ matrix{c_1#0#-c3##-c_1#c_2#0##0#-c_2#c_3} right ]left[ matrix{H_d1##H_d2##H_d3}right ]

Next, q_1, q_2 " and " q_3 values are found out as per equations (1), (2), & (3). Values of h_1, h_2 " and " h_3 are found out as per equations (a), (b) & (c). Next, as stated under heading “Method of calculation for each element”, we check for values for all of h_1, h_2 " and " h_3 . This continues till all of h_1, h_2 " and " h_3 are with the allowed approximation range.